## Slide 1
THERMOPHYSICAL PROPERTIES OF NUCLEAR GRAPHITE IRRADIATED UP TO HIGH NEUTRON FLUENCE
© E.P. Belan and D.V. Khar’kov, 2019
ХI Reactor Material Science Conference
27 - 31 May 2019, Dimitrovgrad

## Slide 2: Introduction
Graphite GR-280 has been used as the material of masonry in the RBMK reactors.
As the graphite masonry serves as a moderator and reflector of neutrons, it is an irreplaceable and partially re-buildable component of the reactor. So it affects the operational life of the power unit at large.
As evidenced by examinations of graphite kernels cut down from the graphite blocks of the RBMK masonry after a 30-year operation, the masonry is in satisfactory condition and thus the reactor can continue operation but it brings about a new task to justify an extended operating life of the masonry.
Purpose of work is to reveal high-dose neutron irradiation effect on the main thermal and physical properties of graphite GR-280 within the irradiation temperature range of 450ºC to 640 °С up to attaining a neutron fluence of 3.31026 m-2.
The samples for irradiation test (830 mm in size) were cut out from standard graphite blocks intended for use in the RBMK reactors.
The graphite samples were under irradiation in the 4th ring of the BOR-60 core (neutron flux density was 1.51019 m-2s-1) at temperatures of 450ºC, 560ºC and 640 °С to attain neutron fluence of (0.1 ÷ 3.2)·1026 m-2 (Еn>0.18 MeV).

## Slide 3: Post-irradiation examination methods
Measurement of specific heat capacity and stored energy
Where ср, срref. are heat capacity values of the sample under examination and reference sample; mref., ms are masses of reference and graphite samples; DSCбаз., DSCref., DSCs. are difference in readings of micro thermal sensing elements when empty crucible, reference and graphite samples are measured .
A measurement error was 3 %.
Application of DSC method with the use of DSC 404 C Pegasus calorimeter.
dS/dТ = а-1·(DSC2 – DSC1)
dS/dТ is a rate of stored energy release; а is a rate of temperature variation; DSC1 and DSC2 are differences in readings of micro thermal sensing elements when the first and second measurements were taken.
A measurement error was 3.5 %.
Schematic representation of DSC 404 C Pegasus

## Slide 4: Post-irradiation examination methods
Thermal conductivity coefficient of samples was obtained by the following formula:
This value was obtained with the use of laser flash method and laser flash apparatus LFA 427. The measurement error was 2.5 %.
Measurement of thermal diffusivity
а = (1.38×h2)/( 2 × 1/2 )
where а is thermal diffusivity, h is a sample thickness, 1/2 is the heating time of the back side of the sample so that to achieve a half of the peak temperature; 1.38 is a non-dimensional coefficient.
Schematic representation of facility
 = а··сp,
where  is thermal conductivity coefficient; а is thermal diffusivity;  is density; сp is specific heat capacity.

## Slide 5
temperature range of 50 ÷ 600°C;
in the environment of helium;
with continuous measurement of sample elongation by inductive displacement transducer with accuracy of 1 µm.
Post-irradiation examination methods
Measurement of thermal linear expansion coefficient
1 – sample; 2 – reference sample; 3 – inductive displacement transducer; 4 – heating element; 5–vacuum enclosure (quartz tube); 6 – power source; 7 – signal transducer; 8 – PC; 9 – furnace control console; 10 – vacuum system; 11 – thermocouples
Schematic representation of facility

## Slide 6
Chart: Measurement temperature, °С
| 27 | 100.5 | 200.1 | 300.39999999999998 | 400.9 | 501.1 | 600.6 | 701.1 | 800.8 | 901.5 | 1000.2 | 1100.0999999999999 | 1200.5999999999999
3,2·10²⁶мˉ² | 5.8968 | 6.7797 | 7.694 | 8.1811 | 8.3822 | 8.2795 | 8.6191 | 9.0943 | 9.5972 | 9.3388 | 10.349 | 9.7395 | 9.6082
1,6·10²⁶мˉ² | 23.803 | 26.7825 | 29.188 | 30.4416 | 30.2427 | 31.2378 | 31.0546 | 31.0611 | 29.599 | 33.2029 | 33.1963 | 37.8341 | 38.2929
0,5·10²⁶мˉ² | 28.0314 | 30.9885 | 33.3587 | 34.2672 | 33.4534 | 33.4636 | 34.2338 | 33.5007 | 34.8021 | 34.8318 | 34.9823 | 42.2013 | 41.411
исх. | 124.8378 | 115.0723 | 101.1498 | 89.0857 | 78.5655 | 72.2562 | 66.2359 | 62.4022 | 58.7566 | 55.2903 | 52.082 | 48.4246 | 46.6742
 | 110
Specific heat capacity and thermal conductivity coefficient
The specific heat capacity of initial and irradiated samples differs by 6% at the highest within the whole measurement temperature range and so the values are within the measurement error.
Where λ is thermal conductivity coefficient, W/(m·K); Сp – specific heat capacity, J/(g·K); А is geometric factor, g/m2; υ is wave propagation velocity of lattice, m/s; l is free path length of phonon, m
Figure 1. Specific heat capacity of initial and irradiated graphite GR-280 and initial graphite POCO against the measurement temperature.
Figure 2. Thermal conductivity coefficient of irradiated and initial graphite against the measurement temperature.
Chart: Сp, J/(g·К)
 | 1.8837
 | 1.5769
 | 1.9

## Slide 7: Thermal conductivity coefficient in relation to neutron fluence and irradiation temperature
Figure 3. Percentage change of the GR-280 thermal conductivity coefficient in relation to neutron fluence.
Chart: Irradiation temperature, °С
| 450 | 560 | 640
ГР-280 5·10²⁵ м⁻² | 34 | 33 | 32
ГР-280 15·10²⁵ м⁻² | 32 | 27 | 24.5
ГР-280 22·10²⁵ м⁻² | 25 | 17 | 13
ГР-280 25·10²⁵ м⁻² | 22 | 13
ГР-280 27·10²⁵ м⁻² | 16 | 10
 | 45
Figure 4. The GR-280 thermal conductivity coefficient in relation to irradiation temperature.
Chart: Neutron fluence, 1026 m-2
| 1.6 | 2.2000000000000002 | 2.59 | 3.05 | 0 | 0.11200000000000002 | 0.5 | 3.2 | 2.75
Тirr = 450 °С | -58.9333 | -68.9189 | -74.9999 | -83.6007 | 0 | -38.4 | -55.3933 | -88.9067 | -78.6667
Тirr = 560 °С | -60 | -33.9706 | -53.3824 | -54.4118 | -75 | -83.8235 | -85.2941
Тirr = 640 °С | -77.8125 | -50.625 | -60.9375
 | -15

## Slide 8
Chart: Neutron fluence, 1026 m-2
| 1.4300000000000002 | 1.97 | 1.1099999999999999 | 1.65 | 0.85399999999999987 | 1.3939999999999999 | 0.52300000000000002 | 0.94600000000000006 | 0
0 | 2.595 | 2.615 | 2.819 | 2.471 | 3.165 | 2.52 | 3.58 | 3.015 | 3.43
90 | 3.81 | 4.232 | 4.098 | 3.865 | 4.603 | 4.081 | 5.435 | 4.514 | 4.44
Chart: Neutron fluence, 1026 m-2
| 0 | 1.8 | 1.6 | 0 | 2.4699999999999998 | 2.2000000000000002 | 0.67900000000000005 | 1.2 | 3.2399999999999998 | 2.95 | 1.65
0 | 3.27 | 2.22 | 2.85 | 3.33 | 2.19 | 2.07 | 3.63 | 3.3 | 3.027 | 2.884 | 2.568
90 | 3.74 | 3.68 | 4.47 | 3.76 | 3.3 | 4.93 | 4.4 | 4.293 | 4.206 | 3.542
Chart: Neutron fluence, 1026 m-2
| 1.7600000000000002 | 0 | 1.7600000000000002 | 2.44 | 0.67900000000000005 | 2.1399999999999997 | 1.25 | 3.12 | 2.8 | 1.55
0 | 1.99 | 3.5 | 2.08 | 2.6 | 3.62 | 2.14 | 2.81 | 3.169 | 3.025 | 2.62
90 | 4.5 | 3.35 | 3.25 | 3.67 | 5.18 | 3.42 | 4.09 | 4.344 | 4.176 | 4.08
TCLE values averaged within a temperature range of 25ºC to 400 °С
TCLE of crystalline particles does not change compared with their initial values when irradiation testing is conducted at temperatures higher than 300 °С.
Thermal linear expansion coefficient (TCLE) in relation to neutron fluence and irradiation temperature
Figure 5. TCLE of graphite exposed to irradiation testing at 450 °С (a), 560 °С (b), and 640 °С (c) in relation to neutron fluence.

## Slide 9: Rate of stored energy release
Figure 6. Rate of stored energy release in annealing of graphite samples irradiated at 450 °С (a) and 640 °С (b) in relation to annealing temperature.
Chart: Annealing temperature, °С
 | 0.35
Chart: Annealing temperature, °С
 | 0.35

## Slide 10: Total stored energy
Chart: Annealing time, s
| 2346.0756000000001 | 2361.0756000000001 | 2376.0756000000001 | 2391.0756000000001 | 2406.0756000000001 | 2421.0756000000001 | 2436.0756000000001 | 2451.0756000000001 | 2466.0756000000001 | 2481.0756000000001 | 2496.0756000000001 | 2511.0756000000001 | 2526.0756000000001 | 2541.0756000000001 | 2556.0756000000001 | 2571.0756000000001 | 2586.0756000000001 | 2601.0756000000001 | 2616.0756000000001 | 2631.0756000000001 | 2646.0756000000001 | 2661.0756000000001 | 2676.0756000000001 | 2691.0756000000001 | 2706.0756000000001 | 2721.0756000000001 | 2736.0756000000001
 | 0.05146 | 0.05683 | 0.050379 | 0.03862 | 0.03581 | 0.03493 | 0.03357 | 0.03227 | 0.02997 | 0.02735 | 0.02477 | 0.02328 | 0.0185 | 0.0141 | 0.01178 | 0.00904 | 0.00743 | 0.00634 | 0.00683 | 0.006 | 0.00538 | 0.00317 | 0.00206 | 0.00053 | 0.00031 | 0.00088 | 0.00101
 | 0.09
Figure 7. Rate of stored energy release during dynamic and isothermal annealing.
Figure 8. Schematic representation of total stored energy estimation.
Figure 9. Total stored energy (S) released in annealing of irradiated samples within a temperature range of 20 ÷ 1300 °С in relation to neutron fluence.
Chart: Neutron fluence, 1026 m-2
| 0 | 0.5 | 1.65 | 3.25
450 °С | 0 | 163 | 190 | 199
650 °С | 0 | 143 | 169 | 174
 | 165
Total stored
energy (S)
Annealing time
dS/dt

## Slide 11: Thermal conductivity coefficient of graphite before and after annealing
Figure 10. Thermal conductivity coefficient of initial and irradiated graphite before and after annealing in relation to measurement temperature.
Figure 11. Percentage change of thermal conductivity coefficient of the sample in relation to the annealing temperature.
Chart: Annealing temperature, °С
| 0 | 600 | 800 | 1000 | 1200
 | -64 | -63 | -61 | -54 | -34
 | 52.5
 | -47.5
Debye equation:
Chart: Measurement temperature, °С
| 25.3 | 100.3 | 200.5 | 300.89999999999998 | 401 | 501 | 601.1 | 701.1 | 801.2 | 901.1 | 1001 | 1100.9000000000001 | 1201.0999999999999
unirrr. | 124.8378 | 115.0723 | 101.1498 | 89.0857 | 78.5655 | 72.2562 | 66.2359 | 62.4022 | 58.7566 | 55.2903 | 52.082 | 48.4246 | 46.6742
before anneal. | 20.567 | 23.1314 | 25.4783 | 26.5038 | 26.4364 | 26.9452 | 27.4384
after anneal. at 600°С | 21.5876 | 24.2909 | 26.6279 | 27.5396 | 27.498 | 27.4874 | 27.4323 | 27.6635 | 28.2245
after anneal. at 800°С | 23.684 | 26.283 | 28.5632 | 29.455 | 29.2421 | 29.3648 | 28.8067 | 29.2599 | 28.8347 | 29.1051 | 29.7458
after anneal. at 1000°С | 29.8929 | 32.861 | 35.1806 | 35.5928 | 34.6547 | 34.2623 | 33.7226 | 34.007 | 32.9381 | 32.4695 | 31.9835 | 32.2639 | 33.4908
after anneal. at 1200°С | 49.4472 | 52.4026 | 53.4014 | 52.2767 | 49.5593 | 48.1737 | 46.398 | 45.4555 | 43.9477 | 39.3326 | 40.0189 | 41.6649 | 43.4657

## Slide 12: Annealing time effect
Figure 12. Thermal conductivity coefficient in relation to annealing time at 1200 °С.
Chart: Annealing time, min
| 0 | 11.3 | 22.7 | 34.4 | 45.4 | 67.400000000000006 | 78.400000000000006 | 89.3 | 100.3 | 116.2 | 127.6 | 138.9
Тобл=550 °С | 35.9565 | 36.4663 | 38.0483 | 36.6491 | 36.9479 | 38.2486 | 37.3311 | 37.6088 | 38.4877 | 38.2416 | 39.5423 | 39.3174
 | 35.5
Straight-line relation;
Rate of change λ is 1.5 W/(m·K) per hour.
Chart: Annealing time, min
| 33.026410000000013 | 33.276410000000013 | 33.526410000000013 | 33.776410000000013 | 34.026410000000013 | 34.276410000000013 | 34.526410000000013 | 34.776410000000013 | 35.026410000000013 | 35.276410000000013 | 35.526410000000013 | 35.776410000000013 | 36.026410000000013 | 36.276410000000013 | 36.526410000000013 | 36.776410000000013 | 37.026410000000013 | 37.276410000000013 | 37.526410000000013 | 37.776410000000013 | 38.026410000000013 | 38.276410000000013 | 38.526410000000013 | 38.776410000000013 | 39.026410000000013 | 39.276410000000013 | 39.526410000000013 | 39.776410000000013 | 40.026410000000013 | 40.276410000000013 | 40.526410000000013 | 40.776410000000013 | 41.026410000000013 | 41.276410000000013 | 41.526410000000013 | 41.776410000000013 | 42.026410000000013 | 42.276410000000013 | 42.526410000000013 | 42.776410000000013 | 43.026410000000013 | 43.276410000000013 | 43.526410000000013 | 43.776410000000013 | 44.026410000000013 | 44.276410000000013 | 44.526410000000013 | 44.776410000000013 | 45.026410000000013 | 45.276410000000013 | 45.526410000000013 | 45.776410000000013 | 46.026410000000013 | 46.276410000000013 | 46.526410000000013 | 46.776410000000013 | 47.026410000000013 | 47.276410000000013 | 47.526410000000013 | 47.776410000000013
 | 0.47508 | 0.4686 | 0.46559 | 0.44869 | 0.39939 | 0.35619 | 0.30474 | 0.26766 | 0.23649 | 0.20938 | 0.19096 | 0.17818 | 0.17245 | 0.15946 | 0.15236 | 0.14142 | 0.13487 | 0.12788 | 0.11879 | 0.1173 | 0.10568 | 0.10177 | 0.095559 | 0.092109 | 0.087279 | 0.084288 | 0.079572 | 0.074283 | 0.069684 | 0.067155 | 0.065889 | 0.059103 | 0.062439 | 0.060483 | 0.05979 | 0.055533 | 0.049548 | 0.047595 | 0.044838 | 0.042537 | 0.045531 | 0.041385 | 0.040581 | 0.041961 | 0.040464 | 0.040233 | 0.038967 | 0.030105 | 0.034137 | 0.030339 | 0.031722 | 0.034365 | 0.028608 | 0.033327 | 0.026997 | 0.026076 | 0.027459 | 0.027921 | 0.025734 | 0.02493
Figure 13. Rate of stored energy release in relation to annealing time.

## Slide 13: Annealing time effect
Figure 14. Thermal conductivity coefficient in relation to measurement temperature.
Chart: Measurement temperature, °С
| 25.5 | 99.6 | 200.3 | 300.39999999999998 | 400.5 | 500.4 | 600.5 | 700.1 | 800.1
Тобл=550 °С | 20.553 | 23.5384 | 25.9221 | 26.9677 | 26.8195 | 27.2098 | 27.4668 | 27.4606 | 27.6918
 | 27.6
 | 36
 | 22
● - measurement data
··· - extrapolation

## Slide 14: Conclusions
1. These experiments made it possible to obtain thermal conductivity coefficient (λ) of graphite GR-280, irradiated in a temperature range of 450 ÷ 650 С up to attaining neutron fluence of 5 ÷ 32·1025 m-2 in relation to a measurement temperature of 25 ÷ 1200 С.
The graph λirr. (at Тtest=Тirr. ) in relation to neutron fluence reveals three stages: the first stage (0 ÷ 51025 m-2) is characterized by a drastic decrease in ∆λ/λinitial that is roughly 55 %; the second stage (51025 m-2 ÷ 151025 m-2) is distinguished by a minor change in ∆λ/λinitial and it is equal to roughly 5 %, and the third stage (higher than 151025 m-2) that exhibits a rapid decrease in ∆λ/λinitial compared to the second stage.
2. It was shown that change in TCLE as a function of neutron fluence reveals 3 stages: the TCLE value tends to increase within the initial section that does not exceed 20 % up to neutron fluence of  (0.5-0.7)1026 m-2 and then TCLE tends to decrease but it tends to increase againt at neutron fluence values higher than Фкр.
The effect of texture on TCLE was revealed: values  are equal to 3.5 in the initial condition and 4.510-6 1/K for graphite samples of parallel and perpendicular cutting, respectively but difference in TCLE values in the perpendicular and parallel directions remains almost the same under irradiation within the entire range of neutron fluence and is roughly 110-6 1/K.

## Slide 15: Conclusions
3. The total stored energy released in annealing within a temperature range from graphite irradiation temperature and up to 1300 °С (irradiated at 450 °С and 640 °С) reaches a constant level at neutron fluence roughly (0.7 ÷ 1.5)·1026 m-2. The peak value of total stored energy is roughly 200 J/g at Тirr. = 450 °С and is roughly 180 J/g at Тirr. = 640 °С. The rate of stored energy release is the maximal one at a temperature of post-irradiation annealing of 1100°С.
4. It was shown that thermal conductivity coefficient of graphite GR-280 irradiated at Тirr. = 450 ÷ 640 °С up to neutron fluence of (0.5 ÷ 1.5)1026 m-2 increases by 19 ÷ 39 W/(mK) (at an ambient temperature) because of thermal annealing at 1200 °С for 2 h. Annealing effect given in absolute values tends to decrease within the above given range of irradiation test parameters as the neutron fluence and irradiation temperature increase but the ratio of thermal conductivity coefficient obtained before and after annealing is a constant value equal to 2.3.

## Slide 16: THANK YOU FOR YOUR ATTENTION!